## Sheet1
D.A.Steam Load Calculator | [6 empty] | Conversion Factors
| Boiler H.P. | 200 | BHP |  | Deg C | 2 | to | 35.6 | Deg F
|  | 13.8 |  |  | Deg F | 70 | to | 21.1111 | Deg C
| City Water Make Up | 45% | MU |  | Gallons of Water | 100 | to | 834.5 | Lbs of Water
|  | 6.21 |  |  | Boiler H.P. | 100 | to | 3349300 | Btu/hr
| DA Operating Temp | 227 | deg F |  | Boiler H.P. | 150 | to | 5175 | Lbs Evaporation
| City Water Make Up Temperature | 55 | deg F |  | Boiler H.P. | 200 | to | 13.8 | GPM Evaporation
|  | 172 |  |  | Sq Ft. EDR | 32 | to | 7680 | Btuh
|  | 534.06 |  |  | Cubic Feet | 50 | to | 374.05 | Gallons
|  | 55% |  |  | Kilograms | 30 | to | 66 | Lbs
| Condensate Return Temperature | 180 |  |  | Parts/million | 32 | to | 1.8688 | Grains/US Gallon
|  | 47 |  |  | CU Ft. Nat Gas | 200 | to | 200800 | Btu/hr
|  | 7.59 |  |  | KW | 100 | to | 341300 | Btu/hr
|  | 178.365 |  |  | Liters | 350 | to | 92.47 | Gallons
| Total Steam Required to Operate D.A. | 712.425 | #/HR |  | Kilograms | 30 | to | 66 | Pounds
| Tank Size Calculator |  |  |  | Heating or Cooling Load on a Water Heat Exchanger
3.14
| Diameter of Tank (in Inches) | 32 | 16 | 803.84 |  |  | GPM | 90 | 500
| Length of Tank (in Inches) | 60 |  | 48230.4 |  |  | Supply Temperature | 180 | Max 212 deg F
|  | 27.9111 |  | 1728 | 40 |  | Return Temperature | 140 | Min 32 deg F
| Full Capacity of Tank | 208.803 | Gallons | 7.481 |  |  |  | 1800000 | Btu's
Feed Tank Calculator
| Boiler H.P. | 250 | BHP
| Feed Tank Size Recommendation | 258.75 | Gallons